# RTF Foundation Data Plan

Jan. 27, 2015 (update date)

Table of Contents

Context	2

Commercial Permafrost Foundation (CCHRC RTF)	2

Data Collection	2

Policies	2

Responsibilities	2

Organization of data	2

Digital Data	3

The BAFoundation logger	3

The Basement logger	5

The Southlabfoundation logger	7

The Northlabfoundation logger	8

Documentation and Metadata	11

Data Documentation	11

Metadata	11

Storage and Security	12

Preservation and Sharing	12

Appendix	13

Data Measurement and Recording Standards	13

Programs	14

Draft Wiring Diagrams	15

# Context

## Commercial Permafrost Foundation (CCHRC RTF)

Purpose: This project is a continuation of the RTF legacy monitoring project that started in 2006. The data has been cleaned up and only error free data and data with specific location information will continue to be collected to inform researchers and building managers of the temperatures under the RTF foundation.

The objectives for this project are:

- To monitor the soil under the foundation of the RTF, in order to inform building maintenance plans.

- To use the temperature data to determine if foundation cooling is necessary under the building addition. If cooling becomes necessary then to use the data to help control the cooling system.

- To develop long term foundation data in a permafrost area to help inform the CRREL permafrost foundation research project.

Funders: CRREL SERDP grant, RTF building fund

Duration: 2006 to ongoing

Folder Locations: \\cabin\CCHRC\Building Science Research\Projects\CRREL Permafrost Fdn 4008-001\Robbin RTF Foundation Stuff

Partners: CRREL, UAF

Proposal Documents: none

## Data Collection

In order to meet the objectives digital data will be collected, stored, and analyzed.  The foundation data will come from 4 CR1000 datalogger stations: BAfoundation, Basement, Southlabfoudation and Northlabfoundation

## Policies

The data will be collected on the logger in hourly and daily averages and exported to the ARSC server once a day. Data will be reviewed for accuracy every six months.

## Responsibilities

The CCHRC data manager is responsible for making certain this data is being collected and is in an error free format.

# Organization of data

#### File structure

Data is recorded on the CR1000 as a time series. Each recording interval becomes a data table. Tables will be programed to output very specific data for future analysis. Raw tables will be stored as .csv files.

#### Naming conventions

Each data point will have a specific name.  All names for the interior sensors will start with the PROJECT_NAME, in this case FOUND. Data names will be as descriptive as possible and end with “_units”

The CR1000 outputs tables based on data time intervals. The data tables will be organized in the best way possible to create meaningful data later, the start of the data table names is “FOUND” and they end with the time interval.

#### Formats and Units

All numbers will be no longer than 4 values after the decimal place. The data starts as a .csv and will be stored as .csv.  All units will be in SI; temperature=°C, moisture content in Vol/Vol

#### Data analysis formats

.csv can be converted into other formats for analysis. Excel and Matlab are two potential formats for analyzed data.

#### Versioning

Raw data files will be appended to with every data upload. If there is a break in data gathering a new file will begin and the old file will be stored as a backup with the dates of the data in the name. Any analyzed data will have the date of the analyzed data in its name. Data should not be overwritten if new analysis takes place, a new version of the data should be saved with a new name that includes the date.

## Digital Data

The 4 CR1000s will collect temperature and soil moisture content data from a variety of locations in the foundation of the building.

The BAFoundation logger collects data from 5 temperature strings that are underneath the foundation of the SNC addition to the RTF. Table 1 lists the names of the data point in the addition foundation. Each name starts with the location under the foundation and then the depth below the surface of the foam (3 ft 4 inch below the surface of the floor). FOUNDBA will be added to the beginning of each name. The holes in the table are due to sensors that do not function, these values are not logged. Figures 1 and 2 show the layout of these strings.

Table 1. BAFoundation Data names

| CTRsurface_C | NEsurface_C | SEsurface_C | SWsurface_C | NWsurface_C |
| --- | --- | --- | --- | --- |
| CTRdepth00_5_C | NEsurface2_C | SEdepth00_5_C | SWdepth00_5_C | NWdepth00_5_C |
| CTRrdepth01_5_C | NEsurface3_C | SEdepth01_5_C | SWdepth01_5_C | NWdepth01_5_C |
| CTRdepth03_0_C | NEsurface4_C |  |  | NWdepth03_0_C |
| CTRdepth06_5_C |  | SEdepth06_5_C | SWdepth06_5_C | NWdepth06_5_C |
|  | NEdepth01_5_C | SEdepth09_0_C | SWdepth09_0_C |  |
| CTRdepth11_0_C | NEdepth03_5_C | SEdepth11_0_C | SWdepth11_0_C | NWdepth11_0_C |
| CTRdepth13_0_C | NEdepth05_5_C |  |  | NWdepth13_0_C |

Figure 1. Building addition sensors with a sample of data. The string starts at the top of the foam, 3 feet, 4 inches below the surface of the floor.

Figure 2. Location of building addition sensors

The Basement logger has two temperature data streams: east of the building baseline and the ICF wall profile. Table 2 lists the data point names for the basement logger. The east base line names include the depth below the surface. Figure 3 shows the layout of the east baseline temperature string. Figure 4 shows the ICF wall profile with the locations of the data points included.

Originally there were 9 moisture content sensors below the basement. Data before 2015 is logged here….Since there is very little location information and the data does not seem to be changing, five to the moisture content sensors are no longer logging. The four remaining moisture content sensors are below the gravel fill but their exact locations are unknown.

Table 2. Basement data point names.

| FOUNDEASTBASE_0_5ft_C | FOUNDICF_INSIDE1_C | FOUND_belowfill12_SM |
| --- | --- | --- |
| FOUNDEASTBASE_1_0ft_C | FOUNDICF_INSIDE2_C | FOUND_belowfill13_SM |
| FOUNDEASTBASE_1_5ft_C | FOUNDICF_INSIDE3_C | FOUND_belowfill14_SM |
| FOUNDEASTBASE_2_0ft_C | FOUNDICF_OUTINNEREPS1_C | FOUND_belowfill_SM |
| FOUNDEASTBASE_2_5ft_C | FOUNDICF_OUTINNEREPS2_C |  |
| FOUNDEASTBASE_3_0ft_C | FOUNDICF_OUTINNEREPS3_C |  |
| FOUNDEASTBASE_3_5ft_C | FOUNDICF_CENTER1_C |  |
| FOUNDEASTBASE_4_0ft_C | FOUNDICF_CENTER2_C |  |
| FOUNDEASTBASE_4_5ft_C | FOUNDICF_CENTER3_C |  |
| FOUNDEASTBASE_5_5ft_C | FOUNDICF_INOUTEREPS1_C |  |
| FOUNDEASTBASE_7_0ft_C | FOUNDICF_INOUTEREPS2_C |  |
| FOUNDEASTBASE_10_0ft_C | FOUNDICF_INOUTEREPS3_C |  |
| FOUNDEASTBASE_12_7ft_C | FOUNDICF_OUTOUTEREPS1_C |  |
| FOUNDEASTBASE_13_2ft_C | FOUNDICF_OUTOUTEREPS2_C |  |
| FOUNDEASTBASE_13_7ft_C | FOUNDICF_OUTSIDE1_C |  |
| FOUNDEASTBASE_14_2ft_C | FOUNDICF_OUTSIDE2_C |  |
| FOUNDEASTBASE_14_7ft_C |  |  |
| FOUNDEASTBASE_15_2ft_C |  |  |
| FOUNDEASTBASE_15_7ft_C |  |  |
| FOUNDEASTBASE_16_2ft_C |  |  |
| FOUNDEASTBASE_16_7ft_C |  |  |
| FOUNDEASTBASE_17_2ft_C |  |  |
| FOUNDEASTBASE_18_2ft_C |  |  |
| FOUNDEASTBASE_20_2ft_C |  |  |
| FOUNDEASTBASE_22_2ft_C |  |  |
| FOUNDEASTBASE_24_2ft_C |  |  |
| FOUNDEASTBASE_26_2ft_C |  |  |
| FOUNDEASTBASE_28_2ft_C |  |  |
| FOUNDEASTBASE_30_2ft_C |  |  |
| FOUNDEASTBASE_32_2ft_C |  |  |
| FOUNDEASTBASE_34_2ft_C |  |  |
| FOUNDEASTBASE_36_2ft_C |  |  |
| FOUNDEASTBASE_38_2ft_C |  |  |
| FOUNDEASTBASE_40_2ft_C |  |  |
| FOUNDEASTBASE_42_2ft_C |  |  |
| FOUNDEASTBASE_44_2ft_C |  |  |
| All base points are in Figure 3 | All ICF wall points are in Figure 4 |  |

East Basement Wall of the RTF

Figure 3. Information on the foundation and the baseline string east of the RTF

Figure 4. ICF wall profile. These sensors are assumed to be in the south wall of the basement.

The Southlabfoundation logger is collecting data from underneath and around the slab foundation in the South lab. Many of the data points for this project have failed but there are enough remaining to continue to the collection. All four of the moisture content sensors in Figure 5 are working.

Table 3. Southlabfoundation data points

| FOUNDSouth_Sjpad_82in_SM | Figure 5 |
| --- | --- |
| FOUNDSouth_Sjpad_33in_SM | Figure 5 |
| FOUNDSouth_Njpad_89in_SM | Figure 5 |
| FOUNDSouth_Njpad_33in_SM | Figure 5 |

Figure 5. South Lab foundation sensors. The red dots are sensor locations, the off color box show the new names of the data points. Only on temperature sensor is working in the south lab.

The Northlabfoundation logger is collecting data from underneath and around the slab foundation in the North lab. Several of the data points for this project have failed but there are enough remaining to continue to the collection.

| FOUNDNorth_Sjpad_33in_C1 | FOUNDNorth_Sjpad_33in_SM | Figure 6 |
| --- | --- | --- |
|  | FOUNDNorth_Sjpad_78in_SM | Figure 6 |
|  | FOUNDNorth_Njpad_33in_SM | Figure 6 |
| FOUNDNorth_Njpad_76_5in_C1 | FOUNDNorth_Njpad_76_5in_SM | Figure 6 |
| FOUNDNorth_slabsurface_C1 (2) |  | Figure 6 |
| FOUNDNorth_bottomslab_C1 (2) |  | Figure 6 |
| FOUNDNorth_west24in_C1 (2) |  | Figure 7 |
| FOUNDNorth_westfooter_C1 |  | Figure 7 |
| FOUNDNorth_middlehalfin_C1 (2,3) |  | Figure 8 |
| FOUNDNorth_middle5in_C1 (2.3) |  | Figure 8 |
| FOUNDNorth_middle10in_C1 (2.3) |  | Figure 8 |

Figure 6. North lab, north wall test section. The red dots are sensors locations, the new names of the sensors are in the off color boxes.

Figure 7. North lab west wall test section. Only two of these temperature sensors are working.

Figure 8. Sensors in the side, middle and corner locations of the North Lab, exact locations are unknown.

# Documentation and Metadata

## Data Documentation

All digital data and documentation for this project will be stored here \\cabin\CCHRC\Building Science Research\Projects\CRREL Permafrost Fdn 4008-001\Robbin RTF Foundation Stuff

Raw sensor data will also be stored at the Arctic Regions Supercomputer Center (ARSC) at UAF.

Each researcher on this project maintains an independent lab notebook where they may record information related to this project in the form of rough notes. That information will get a label “FOUNDATION” to make those notes easy to find if they become necessary.

## Metadata

Data on the sensors is the most important data in this project and needs to follow a very specific format. There is an overall data standards document outlined below. In addition, each data table will have its own metadata document; the components of the table metadata are outlined below.

#### Data Standards

Detailed data standards are appended to this document.  The data standards include details about each sensor, its purpose, location, program, and output files.  The CR1000 programs and wiring diagrams are appended to the data standards

Data standards and wiring diagrams will be kept in \\cabin\CCHRC\Building Science Research\Projects\CRREL Permafrost Fdn 4008-001\Robbin RTF Foundation Stuff and updated every 6 months.

#### Table Metadata

Each table will have a metadata spreadsheet that includes all of the following data points:

| File Name | Exact name of the file |
| --- | --- |
| Headers Included (Y/N) | Are column headers in the file? (Y/N) |
| Delimitation Type | What is used to separate data columns? (comma, space, tab, etc.) |
| File Extension | What is the file extension type? |
| Number of Header Lines Total | How many header lines are in the data file? |
| Column # | Which column of data are the following descriptions referring to? |
| Name / Title | What is the data point called? |
| Definition of Name / Title | a detailed description of the data point name. |
| Units | Unit label for measurements. (cm, degC,%, etc.) |
| Storage Type | string (text variable), integer (whole number), float point (digits representing real number), date (temporal reference) |
| Location, building | which building houses the sensor |
| Location, level | what level or floor of the building is the sensor located |
| Location, details | where exactly is the sensor using a fixed reference point, list the point, attach photos if possible |
| Notes | Note strange occurrence or errors |
| Min Valid Value | Minimum expected value for this measurement. (Normal Range) |
| Max Valid Value | Maximum expected value for this measurement. (Normal Range) |
| Error Code | Any error codes that may be present in the data |
| Precision (Decimal Places) | Please give the number of decimal places expressed in the data. |
| Calculation Notes | Information about calculations performed to derive this value. |

# Storage and Security

Sensor data will be stored here: \\cabin.cchrc.uaf.edu\CCHRC, as well as at ARSC at UAF. Both locations will back up the data to tape at least once a week. All data in both locations will be password protected. Data will be available in a limited fashion from a web interface on the ARSC site.

# Preservation and Sharing

This is a long term data collection project the data will remain on the ARSC site for CCHRC data and be accessible to future researchers.

# Appendix

## Data Measurement and Recording Standards

Last Update: Dec. 2, 2014

Last Update By: Robbin

All data will be collected by Campbell Scientific CR1000 dataloggers. The loggers will be connected to the CCHRC network and will be send data to a web server via FTP every day.

The 4 loggers have the following connection parameters.

|  | IP internal | PakAddress | IP external |
| --- | --- | --- | --- |
| Basement | 172.20.127.46 | 50 | 137.229.65.13 |
| Northlabfound | 172.20.127.44 | 80 | 137.229.65.11 |
| Bafoundation | 172.20.127.59:6786 | 1 | 137.229.65.59:6786 |
| Southlabfound | 172.20.127.45 | 30 | 137.229.64.143 |

There are 2 types of sensors in the foundation: GWS thermistors and Campbell Scientific CS616-L Water Content Reflectometers.

Sensor: GWS direct bury thermistors with 10kΩ resistors

Measurement Range:  -80°C to 150°C ±0.1°C

Output Units:  temp in ° C

Scan Interval: 5 minute

Averaging Interval: daily

Algorithms: using the CR1000 programing

Const a = 0.0014654354

Const b = 0.0002386780

Const c = 0.0000001000

BrHalf (therm(I),1,mV2500,1,Vx1,1,2500,True ,0,_60Hz,1.0,0)

I = I + 1

For I=1 To 123

GWS_Therm_kOHM(I) = Rf_1*therm(I)/(1-therm(I))

Next I

For I=1 To 123

D(I) = LN (1000*GWS_Therm_kOHM(I))                          'ln resistance (ohm)

GWS_T_deg_C(I) = (1/(a + b*D(I) + c*(D(I))^3)) - 273.15     'Steinhart & Hart Equation

Next I

Sensor: Campbell Scientific CD 616-l Water Content Reflectometer

Measurement Range:  0% to saturation volumetric water content in soils between 0°C and 70°C

Output Units:  Volume water/Volume of soil

Scan Interval: 5 minute

Averaging Interval: daily

Algorithms: for the CR1000

If IfTime (0,5,Min) Then      'BEGIN 5-MINUTE MEASUREMENT LOOP

'READ 10 CS616 SOIL MOISTURE SENSORS

CS616 (CS616_us(),10,5,5,10,1.0,0)

For I = 1 To 10

'CONVERT SOIL MOISTURE SENSOR MEASUREMENT (micro-seconds) TO VOLUMETRIC

'  SOIL WATER CONTENT

CS616_SM(I) = -0.0663+CS616_us(I)*(-0.0063+CS616_us(I)*0.0007)

Next I

EndIf

Notes from the manual:

The water content reflectometer measures volumetric water content. Soil water content is expressed on a gravimetric and a volumetric basis. To obtain the independently determined volumetric water content, gravimetric water content must first be measured. Gravimetric water content (θg) is the mass of water per mass of dry soil. It is measured by weighing a soil sample (mwet), drying the sample to remove the water, then weighing the dried soil (mdry).

θg=mwatermsoil=mwet-mdrymdry

Volumetric water content (θv) is the volume of liquid water per volume of soil. Volume is the ratio of mass to density (ρb) which gives:

θv=volumewatervolumesoil=mwaterρwatermsoilρsoil=θg*ρsoilρwater

The density of water is close to 1 and often ignored.

There is a metadata spreadsheet for each data table.

## Programs

Draft Wiring Diagrams