# Heat Pump Demonstration Data Plan

January 1, 2014

Table of Contents

Context	2

RTF Ground Source Heat Pump Demonstration Project	2

Data Collection	2

Ground Loop Data	2

Equipment Performance Data	3

Other Data Sources	5

Policies	5

Responsibilities	5

Organization of data	5

Documentation and Metadata	6

Data Documentation	6

Metadata	6

Storage and Security	7

Preservation and Sharing	7

Appendix	8

RTF GSHP Demonstration	8

Data Measurement and Recording Standards	8

Ground Loop Data Collection	8

Manifold Temperature	11

Draft CR1000 Program	14

Draft Wiring Diagrams	22

# Context

## RTF Ground Source Heat Pump Demonstration Project

Purpose:

The objectives for installing and monitoring a GSHP at CCHRC’s facility are to:

- Determine if long-term performance of a GSHP is stable in a severe cold climate, and thoroughly characterize its efficiency over multiple heating seasons.

- Evaluate if thermal degradation of the ground loop field is a fundamental challenge for adoption of the technology in cold climates.

- Examine the significance of practical and affordable ground surface treatments to maximize energy capture in the ground.

- Compare the primary energy consumption and greenhouse gas emissions of the GSHP installation relative to conventional heating systems.

- Demonstrate the viability of a GSHP at its most northern (coldest) limit of operation.

Funders: Alaska Energy Authority (AEA)-Emerging Energy Tech Fund (EETF)

Duration: September 2012 to July 2016

Folder Locations: \\cabin.cchrc.uaf.edu\CCHRC\Building Science Research\Projects\RTF heat pump demonstration

Partners: Institute of Northern Engineering (INE) at University of Alaska Fairbanks (UAF), Alaska Geothermal LLC

Proposal Documents: \\cabin.cchrc.uaf.edu\CCHRC\Building Science Research\Projects\RTF heat pump demonstration\EETF Proposal Docs

## Data Collection

In order to meet the objectives several streams of data will be collected, stored, and analyzed.  Four types of data will be collected; ground loop data, equipment performance data, system notes, and installation and maintenance cost data.

The ground loop and equipment performance will be physically monitored with a variety of sensors.  All of the sensors will be connected to a data logging system on the CCHRC Insight server that will record raw data from each sensor and format that data into useable data files. The data files will be exported to both local and remote webservers. The installation and maintenance cost data will be collected throughout the course of the project as costs become apparent.  This cost data will also be stored on both local and remote webservers. Raw data from the ground loop and equipment performance data logger will be exported to ACEP’s data server once a week via FTP.

### Ground Loop Data

Instrumentation of the heat pump system will include three thermistor temperature sensor strings within the horizontal ground loop and two sensor strings in undisturbed ground as a baseline. A sixth temperature string will run horizontally across the top of the ground loops just below the surface and out to the baseline strings.  The temperature sensors will enable the analysis of how the heat pump affects the thermal regime of the ground and the degree to which the ground recovers heat. This pertains to the second and third research objectives stated above. Each string will have multiple sensors that reach to varying depths in the active layer (i.e. above the underlying permafrost). The sensors will be placed similar to the layout in Figure 1.

Figure 1. Schematic of Ground Temperature Sensors. More detailed information about the ground sensors is available in the appendix.

Data from the thermistor strings will be recorded using a Campbell Scientific CR1000 datalogger (pak address 110).  The sensors will be scanned every 2 minutes and average data will be recorded hourly and daily.

### Equipment Performance Data

The heat pump and circulating pumps will be monitored for electrical consumption. BTU meters on the ground loop and hydronic heat distribution sides of the heat pump will be used to monitor the energy in and out of the heat pump. The data will be collected via a CR 1000 . Figure 2 shows the conceptual layout of the heat pump system and rough location of the sensors. This equipment will help researchers address objectives 1, 2, and 5 listed above.

Figure 2. Conceptual schematic for the RTF heat pump system with instrumentation. More detailed information about the in-building sensors is available in the appendix.

#### System notes

Operational notes and maintenance logs will be recorded in a lab notebook that the building operations assistant maintains and keeps. Significant events will be copied over to CCHRC’s internal wiki as time allows.

#### Installation and Maintenance Cost Data

Beyond the potential for energy savings for an individual building, a key consideration in evaluating heat pump performance is determining whether it provides a net benefit when considering primary energy consumption and greenhouse gas emissions associated with electricity generation. By understanding the long-term efficiency of GSHPs, a comparison of GSHPs to conventional heating methods (e.g. heating oil) can be conducted via a life cycle cost analysis (LCCA). This effort will closely track all the costs associated with the GSHP, from initial purchase and transport of materials to installation. Electricity use will be monitored, routine service and repair costs tracked, and costs for replacement of major components if necessary will be tracked as well.  This data will be logged into a spreadsheet format and stored on the local CCHRC server as well as the remote CCHRC webserver. This set of data will enable researchers to address objective 4 listed above.

### Other Data Sources

#### Weather Data

Weather data will be necessary for some of the analysis of the heat pump system. In particular temperature and solar radiation will be important in studying the thermal regime in the ground loop. CCHRC has a weather station on the roof of its building. The data from the weather station is currently logged on hourly and daily intervals and uploaded to an external data server daily. CCHRC will pull data from the weather station data as needed and save the excerpted data on the local CCHRC data server.

#### Potential Data

There may be other data streams that become necessary in the course of the project. For example the masonry stove also heats this portion of the building; it may become necessary to look at data from the masonry stove as part of this project. The masonry stove as well as other heating system points are monitored by the building’s Siemens control system and can be accessed at any time if needed.

## Policies

CCHRC will provide quarterly updates to AEA (both fiscal and physical status updates)

## Responsibilities

Robbin Garber-Slaght and Colin Craven are the PIs for this project. Robbin is the project manager making sure all steps of the project are completed in compliance with the grant language and this data management plan. The data management plan will be revisited once the data system is running.

# Organization of data

#### File structure

Data is recorded on the CR1000 as a time series. Each recording interval becomes a data table. Tables will be programed to output very specific data for future analysis. Raw tables will be stored as .csv files.

The CR1000 has the capability of creating calculated data points. These calculated data points will be stored in separate table files.

#### Naming conventions

Each data point will have a specific name.  All names for the interior sensors will start with RTFGSHP; all names from the ground loop will start with GL. Data names will be as descriptive as possible and end with “_units”

The CR1000 outputs tables based on data time intervals. The data tables will be organized in the best way possible to create meaningful data later, the start of the data table name is RTFGSHP and end with the time interval.

#### Formats and Units

All numbers will be no longer than 4 values after the decimal place. The data starts as a .csv and will be stored as .csv.  All units will be in SI; temperature=°C, energy rate = kW, flow rate = L/min, total energy=kWh

#### Data analysis formats

.csv will be converted into other formats for analysis. Excel and Matlab are two potential formats for analyzed data.

#### Versioning

Raw data files will be appended to with every data upload. If there is a break in data gathering a new file will begin and the old file will be stored with the dates of the data in the name. Any analyzed data will have the date of the analyzed data in its name. Data should not be overwritten if new analysis takes place, a new version of the data should be saved with a new name that includes the date.

# Documentation and Metadata

## Data Documentation

All digital data and documentation for this project will be stored here \\cabin.cchrc.uaf.edu\CCHRC\Building Science Research\Projects\RTF heat pump demonstration\Data. Raw sensor data will also be stored at the Arctic Regions Supercomputer Center (ARSC) at UAF.

Each researcher on this project maintains an independent lab notebook where they may record information related to this project in the form of rough notes. That information will get a label “RTFGSHP” to make those notes easy to find if they become necessary.

There is a binder for this project labeled RTFGHSP that resides on the PM’s desk and holds papers that may not have been digitized. Manuals for instruments and equipment are to be kept in this binder.

## Metadata

Data on the sensors is the most important data in this project and needs to follow a very specific format. There is an overall data standards document outlined below. In addition, each data table will have its own metadata document; the components of the table metadata are outlined below.

#### Data Standards

Detailed data standards are appended to this document.  The data standards include details about each sensor, its purpose, location, program, and output files.  The CR1000 programs and wiring diagrams are appended to the data standards

Data standards and wiring diagrams will be kept in \\cabin.cchrc.uaf.edu\CCHRC\Building Science Research\Projects\RTF heat pump demonstration\Metadata and updated on a semi-monthly basis.

#### Table Metadata

Each table will have a metadata document that includes all of the following data points:

Project title:

Project description:

Keywords:

Study period:

Site/location:

Data Column info:

Variable Name

Description

Units

Data type

Location/building

Location/level

Location/details

Notes

Error

Sensor Type

Calibration equation

# Storage and Security

Sensor data will be stored here: \\cabin.cchrc.uaf.edu\CCHRC\Building Science Research\Projects\RTF heat pump demonstration\Data, as well as at ARSC at UAF. Both locations will back up the data to tape at least once a week. All data in both locations will be password protected. Data will be available in a limited fashion from a web interface on the ARSC site.

# Preservation and Sharing

This phase of the project will monitor the heat pump for three years and culminate in a research report using the collected data. The project is designed to last for at least 10 years of data collection. At the end of those ten years the data will remain on the ARSC site for CCHRC RTF data and be accessible to future researchers.

# Appendix

## RTF GSHP Demonstration

## Data Measurement and Recording Standards

Last Update: 3/20/13

Last Update By: Robbin

All data will be collected by 2 CR100 dataloggers. The loggers will be connected to the CCHRC network and will be send data to a web server via FTP once a week.

### Ground Loop Data Collection

#### Frost Tubes

Manual data collection once a month, on or near the 1st. This data will be recorded in the system notes notebook and transferred to the CCHRC internal wiki as time allows. \\cabin.cchrc.uaf.edu\CCHRC\Building Science Research\Projects\RTF heat pump demonstration\Data

Main Questions: Does the ground loop create local permafrost?

Two tubes within the ground loop field and one outside the field will be down to a depth of about 10 feet. Following the directions laid out here, http://ine.uaf.edu/werc/projects/permafrost/howto.pdf

#### In-ground Temperature Sensors

A temperature multiplexer is connected to a CR1000 outside attached to the ground loop fencing. It will communicate with the CCHRC network via the Freewave network. ()

Main Questions: How does the ground temperature change within the heat pump ground loop? How do different surface treatments affect the ground temperature regime?

Sensor: NTC Thermistors, US Sensor PS103J2

Measurement Range:  -80°C to 150°C ±0.1°C

Output Units:  temp in ° C

Scan Interval: 10 minutes

Averaging Interval: hourly, daily

Algorithm: using Campbell Scientific CR1000

PortSet (1 ,1 )         'TURN ON AM16/32 #1 MULTIPLEXER, SET PORT 1 HIGH

I = 1                   'INITIALIZE INDEX INTERGER I TO ONE

SubScan (0,sec,13)  ‘4 SETS OF 14 THERMISTORS (49 GROUND TEMPS+6 MANIFOLD )

Delay (0,10,mSec)

PulsePort (2,10000)    'ADVANCE AM16/32

BrHalf (therm(I),4,mV2500,1,Vx1,4,2500,True ,0,_60Hz,1.0,0)

I = I + 4

NextSubScan

PortSet (1 ,0 )        'TURN ONFFAM16/32 #1 MULTIPLEXER, SET PORT 1 LOW

'CONVERT MEASURED VOLTAGE RATIO TO RESISTANCE (kOHM) FOR  THERMISTORS

For I=1 To 40

Therm_kOHM(I) = 10*therm(I)/(1-therm(I))

Next I

' THERMISTOR RESISTANCE To deg c For 52 THERMISTORS

For I=1 To  52

D(I) = LN (1000*Therm_kOHM(I))                          'ln resistance (ohm)

Temp_C(I) = (1/(a + b*D(I) + c*(D(I))^3)) - 273.15     'Steinhart & Hart Equation

Next I

Const a = 0.0011253

Const b = 0.000234

Const c = 0.0000000856

[Const agw = 0.001468, Const bgw = 0.0002383,Const cgw = 0.0000001007 for GWS thermistors)

West  temp string – 4 meters west of the ground loop, at the edge of the UAF field, it has a frost tube

| Depth (m) | Depth (ft) | Wire Color | Cable Color | Name |
| --- | --- | --- | --- | --- |
| 0 | 0 | Orange/w | Red/red | GL_westsurface_C |
| 0.25 | 0.8 | Orange | red/red | GL_westquarterm_C |
| 0.75 | 2.5 | Blue | red/red | GL_west3quarterm_C |
| 1 | 3.3 | Brown | red/red | GL_west1m_C |
| 1.5 | 5 | Brown/w | red/red | GL_west1andhalfm_C |
|  |  | Green/w=ground | Red/red |  |
| 2 | 6.5 | orange | red/red/red | GL_west2m_C |
| 2.7 | 9 | blue | red/red/red | GL_west2point7m_C |
| 3.2 | 10.5 | brown | red/red/red | GL_west3point2m_C |
| 3.7 | 12 | green | red/red/red | GL_west3point7m_C |

East temp string –4 meter east of the ground loop, 3 meters east of the fence in-line with the datalogger box

| Depth (m) | Depth (ft) | Wire Color | Cable Color | Name |
| --- | --- | --- | --- | --- |
| 0 | 0 | Orange/w | Green/green | GL_eastsurface_C |
| 0.25 | 0.8 | Orange | green/green | GL_eastquarterm_C |
| 0.75 | 2.5 | Blue | green/green | GL_east3quarterm_C |
| 1 | 3.3 | Brown | green/green | GL_east1m_C |
| 1.5 | 5 | green/w | green/green | GL_east1andhalfm_C |
|  |  | Green=ground | green/green |  |
| 2 | 6.5 | orange | green/green/green | GL_east2m_C |
| 2.7 | 9 | Blue | green/green/green | GL_east2point7m_C |
| 3.2 | 10.5 | brown | green/green/green | GL_east3point2m_C |
| 3.7 | 12 | green | green/green/green | GL_east3point7m_C |

#### Horizontal temp string- just under the surface across the top of the loop field and beyond

| Distance from the edge of loop field |  |  |  | Wire Color |  | Cable Color |  | Name |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 m |  | 0 m |  | orange |  | orange/orange |  | GL_Horzeast0m_C |
| 0 m |  | 3.3 ft |  | Blue |  | orange/orange |  | GL_horzeast1m_C |
| 2 m |  | 6.5 ft |  | brown |  | orange/orange |  | GL_horzeast2m_C |
| 3 m |  | 9.8 ft |  | green |  | orange/orange |  | GL_horzeast3m_C-not recording |
| 4 m |  | 13.1 ft |  | on the top of the east string, GL_eastsurface_C do not build |  |  |  |  |
| Distance from the edge of loop field |  |  | Wire Color |  | Cable Color |  | Name |  |
| 0 m | 0 ft |  | orange |  | orange |  | GL_horzwest0m_C |  |
| 1 m | 3.3 ft |  | Blue |  | orange |  | GL_horzwest1m_C |  |
| 2 m | 6.5 ft |  | brown |  | orange |  | GL_horzwest2m_C |  |
| 3 m | 9.8 ft |  | green |  | orange |  | GL_horzwest3m_C* |  |
| 4m | 13.1 ft |  | on the top of the west string, GL_westsurface_C do not build |  |  |  |  |  |

*reading error

Three loops will be within the loop field along the centerline

#### West loop temp string-between loops 5 and 6 (the farthest west) 50 feet from the end of the trenches

| Depth (m) | Depth (ft) | Wire Color | Cable Color | Name |
| --- | --- | --- | --- | --- |
| 0 | 0 | blue/w | Black/black/black | GL_westloopsurface_C |
| 0.25 | 0.8 | Orange | black/black/black | GL_westloopquarterm_C |
| 0.75 | 2.5 | Blue | black/black/black | GL_westloop3quarterm_C |
| 1 | 3.3 | Brown | black/black/black | GL_westloop1m_C |
| 1.5 | 5 | Brown/w | black/black | GL_westloop1andhalfm_C* |
|  |  | Green=ground | Black/black/black |  |
| 2 | 6.5 | Orange | black/black | GL_westloop2m_C |
| 2.7 | 9 | Blue | black/black | GL_westloop2point7m_C |
| 3.2 | 10.5 | Brown | black/black | GL_westloop3point2m_C |
| 3.7 | 12 | Blue/w | black/black | GL_westloop3point7m_C |
|  |  | Green=ground |  |  |

*reading error until 10.9.14, rewired and corrected on 10.9.14

#### East loop temp string-in the middle of the 2nd loop, 41 feet from the south end of the trench

| Depth (m) | Depth (ft) | Wire Color | Cable Color | Name |
| --- | --- | --- | --- | --- |
| 0 | 0 | Orange/w | Yellow/yellow | GL_eastloopsurface_C |
| 0.25 | 0.8 | Orange | Yellow/yellow | GL_eastloopquarterm_C |
| 0.75 | 2.5 | Blue | Yellow/yellow | GL_eastloop3quarterm_C |
| 1 | 3.3 | Brown | Yellow/yellow | GL_eastloop1m_C |
| 1.5 | 5 | Brown/w | Yellow/yellow | GL_eastloop1andhalfm_C |
|  |  | Green=ground | Yellow/yellow |  |
| 2 | 6.5 | Blue | Yellow/yellow/yellow | GL_eastloop2m_C |
| 2.7 | 9 | Brown | Yellow/yellow/yellow | GL_eastloop2point7m_C |
| 3.2 | 10.5 | orange | Yellow/yellow/yellow | GL_eastloop3point2m_C |
| 3.7 | 12 | green | Yellow/yellow/yellow | GL_eastloop3point7m_C |

#### Center loop temp string – GWS string – in the middle of the 4th loop, 50 feet from the end of the trenches, this string is made of a combination of GWS sensors and new PS type sensors there are some different constants, see the attached program

| Depth (m) | Depth (ft) | Wire Color | Cable Color | Name |
| --- | --- | --- | --- | --- |
| 0 | 0 | Black | White | GL_centersurface_C |
| 0.3 | 1 | Blue | White | GL_centerquarterm_C |
| 0.6 | 2 | Brown | White | GL_center3quarterm_C |
| 1 | 3.5 | Green | White | GL_center1m_C |
| 2.1 | 7 | Grey (new PS type) | White | GL_center2point1m_C |
| 2.9 | 9.5 | Orange | White | GL_center2point9m_C |
| 3.5 | 11.5 | Red | White | GL_center3andhalfm_C |
| 4.1 | 13.5 | Violet (new PS type) | White | GL_center4point1m_C |

## GSHP GL CR1000 program

#### 'Program Name RTF_GSHP_Ground_temp

#### 'date 10.9.14

#### 'changes to correct to backwards wiring of west loop

#### 'date 10/14/2013

#### 'changes to bring variable names into compliance with DMP

#### Public StationID

#### Public Therm_kOhm(52), Temp_C(52), therm(52)

#### Public LoggerTemp_C, BattVolts_V

#### Dim i

#### Dim D(56)

#### '  For thermistors -- conversion of kOHM to deg C

#### Const a = 0.0011253

#### Const b = 0.000234

#### Const c = 0.0000000856

#### Const agw = 0.001468

#### Const bgw = 0.0002383

#### Const cgw = 0.0000001007

#### Alias Temp_C(1) = GL_westsurface_C

#### Alias Temp_C(2) = GL_westquarterm_C

#### Alias Temp_C(3) = GL_west3quarterm_C

#### Alias Temp_C (4)= GL_west1m_C

#### Alias Temp_C (5)= GL_west1andhalfm_C

#### Alias Temp_C (6)= GL_west2m_C

#### Alias Temp_C (7)= GL_west2point7m_C

#### Alias Temp_C (8)= GL_west3point2m_C

#### Alias Temp_C (9)= GL_west3point7m_C

#### Alias Temp_C(10) = GL_eastsurface_C

#### Alias Temp_C(11) = GL_eastquarterm_C

#### Alias Temp_C(12) = GL_east3quarterm_C

#### Alias Temp_C (13)= GL_east1m_C

#### Alias Temp_C (14)= GL_east1andhalfm_C

#### Alias Temp_C (15)= GL_east2m_C

#### Alias Temp_C (16)= GL_east2point7m_C

#### Alias Temp_C (17)= GL_east3point2m_C

#### Alias Temp_C (18)= GL_east3point7m_C

#### Alias Temp_C (19)= GL_horzeast0m_C

#### Alias Temp_C (20)= GL_horzeast1m_C

#### Alias Temp_C (21)= GL_horzeast2m_C

#### Alias Temp_C (22)= GL_horzeast3m_C

#### Alias Temp_C (23)= GL_horzwest0m_C

#### Alias Temp_C (24)= GL_horzwest1m_C

#### Alias Temp_C (25)= GL_horzwest2m_C

#### Alias Temp_C (26)= GL_horzwest3m_C

#### Alias Temp_C(27) = GL_westloop3point7m_C

#### Alias Temp_C(28) = GL_westloop2m_C

#### Alias Temp_C(29) = GL_westloop2point7m_C

#### Alias Temp_C (30)= GL_westloop3point2m_C

#### Alias Temp_C (31)= GL_westloop1andhalfm_C

#### Alias Temp_C (32)= GL_westloopquarterm_C

#### Alias Temp_C (33)= GL_westloop3quarterm_C

#### Alias Temp_C (34)= GL_westloop1m_C

#### Alias Temp_C (35)= GL_westloopsurface_C

#### Alias Temp_C(36) = GL_eastloopsurface_C

#### Alias Temp_C(37) = GL_eastloopquarterm_C

#### Alias Temp_C(38) = GL_eastloop3quarterm_C

#### Alias Temp_C (39)= GL_eastloop1m_C

#### Alias Temp_C (40)= GL_eastloop1andhalfm_C

#### Alias Temp_C (41)= GL_eastloop2m_C

#### Alias Temp_C (42)= GL_eastloop2point7m_C

#### Alias Temp_C (43)= GL_eastloop3point2m_C

#### Alias Temp_C (44)= GL_eastloop3point7m_C

#### Alias Temp_C(45) = GL_centersurface_C

#### Alias Temp_C(46) = GL_centerquarterm_C

#### Alias Temp_C(47) = GL_center3quarterm_C

#### Alias Temp_C (48)= GL_center1m_C

#### Alias Temp_C (49)= GL_center2point1m_C

#### Alias Temp_C (50)= GL_center2point9_C

#### Alias Temp_C (51)= GL_center3andhalfm_C

#### Alias Temp_C (52)= GL_center4point1m_C

#### 'STATION ID

#### StationName (RTF_GSHP_Ground_Temp)

#### '\\\\\\\\\\\\\\\\\\\\\\\\ OUTPUT SECTION ////////////////////////

#### DataTable(GL_HourlyDiag, true, -1)

#### DataInterval(0,60,Min,10)

#### Sample(1, StationID, FP2)

#### Average (1,LoggerTemp_C,FP2,False)

#### Average (1,BattVolts_V,FP2,False)

#### EndTable

#### DataTable (GL_groundtemprawhr, true, -1)

#### DataInterval (0,60,min,10)

#### Average (52,therm(),FP2,False)

#### Average (52,Temp_C(),FP2,False)

#### EndTable

#### DataTable (GL_westgroundtempday, true, -1)

#### DataInterval(0,24,hr,10)

#### Average(1,GL_westsurface_C, fp2,false)

#### Average(1,GL_westquarterm_C, fp2,false)

#### Average(1,GL_west3quarterm_C, fp2,false)

#### Average(1,GL_west1m_C, fp2,false)

#### Average(1,GL_west1andhalfm_C, fp2,false)

#### Average(1,GL_west2m_C, fp2,false)

#### Average(1,GL_west2point7m_C, fp2,false)

#### Average(1,GL_west3point2m_C, fp2,false)

#### Average(1,GL_west3point7m_C, fp2,false)

#### EndTable

#### DataTable (GL_eastgroundtempday, true, -1)

#### DataInterval(0,24,hr,10)

#### Average(1,GL_eastsurface_C, fp2,false)

#### Average(1,GL_eastquarterm_C, fp2,false)

#### Average(1,GL_east3quarterm_C, fp2,false)

#### Average(1,GL_east1m_C, fp2,false)

#### Average(1,GL_east1andhalfm_C, fp2,false)

#### Average(1,GL_east2m_C, fp2,false)

#### Average(1,GL_east2point7m_C, fp2,false)

#### Average(1,GL_east3point2m_C, fp2,false)

#### Average(1,GL_east3point7m_C, fp2,false)

#### EndTable

#### DataTable (GL_westloopgtempday, true, -1)

#### DataInterval(0,24,hr,10)

#### Average(1,GL_westloopsurface_C, fp2,false)

#### Average(1,GL_westloopquarterm_C, fp2,false)

#### Average(1,GL_westloop3quarterm_C, fp2,false)

#### Average(1,GL_westloop1m_C, fp2,false)

#### Average(1,GL_westloop1andhalfm_C, fp2,false)

#### Average(1,GL_westloop2m_C, fp2,false)

#### Average(1,GL_westloop2point7m_C, fp2,false)

#### Average(1,GL_westloop3point2m_C, fp2,false)

#### Average(1,GL_westloop3point7m_C, fp2,false)

#### EndTable

#### DataTable (GL_eastloopgtempday, true, -1)

#### DataInterval(0,24,hr,10)

#### Average(1,GL_eastloopsurface_C, fp2,false)

#### Average(1,GL_eastloopquarterm_C, fp2,false)

#### Average(1,GL_eastloop3quarterm_C, fp2,false)

#### Average(1,GL_eastloop1m_C, fp2,false)

#### Average(1,GL_eastloop1andhalfm_C, fp2,false)

#### Average(1,GL_eastloop2m_C, fp2,false)

#### Average(1,GL_eastloop2point7m_C, fp2,false)

#### Average(1,GL_eastloop3point2m_C, fp2,false)

#### Average(1,GL_eastloop3point7m_C, fp2,false)

#### EndTable

#### DataTable (GL_centerlooptempday, true, -1)

#### DataInterval(0,24,hr,10)

#### Average(1,GL_centersurface_C, fp2,false)

#### Average(1,GL_centerquarterm_C, fp2,false)

#### Average(1,GL_center3quarterm_C, fp2,false)

#### Average(1,GL_center1m_C, fp2,false)

#### Average(1,GL_center2point1m_C, fp2,false)

#### Average(1,GL_center2point9_C, fp2,false)

#### Average(1,GL_center3andhalfm_C, fp2,false)

#### Average(1,GL_center4point1m_C, fp2,false)

#### EndTable

#### DataTable (GL_surfacetemphr, true, -1)

#### DataInterval(0,60,Min,10)

#### Average(1,GL_horzeast0m_C, fp2,false)

#### Average(1,GL_horzeast1m_C, fp2,false)

#### Average(1,GL_horzeast2m_C, fp2,false)

#### 'Average(1,GL_horzeast3m_C, fp2,false)

#### Average(1,GL_horzwest0m_C, fp2,false)

#### Average(1,GL_horzwest1m_C, fp2,false)

#### Average(1,GL_horzwest2m_C, fp2,false)

#### Average(1,GL_horzwest3m_C, fp2,false)

#### Average (1,GL_centersurface_C, fp2,false)

#### Average (1,GL_eastsurface_C, fp2,false)

#### Average (1,GL_eastloopsurface_C, fp2,false)

#### Average (1,GL_westsurface_C, fp2,false)

#### Average (1,GL_westloopsurface_C, fp2,false)

#### EndTable

#### DataTable (GL_quartertemphr, true, -1)

#### DataInterval(0,60,Min,10)

#### Average (1,GL_centerquarterm_C, fp2,false)

#### Average (1,GL_eastquarterm_C, fp2,false)

#### Average (1,GL_eastloopquarterm_C, fp2,false)

#### Average (1,GL_westquarterm_C, fp2,false)

#### Average (1,GL_westloopquarterm_C, fp2,false)

#### EndTable

#### '\\\\\\\\\\\\\\\\\\\\\\\\\\\ PROGRAM ////////////////////////////

#### BeginProg

#### Scan(120,Sec, 3, 0)

#### Battery(BattVolts_V)

#### PanelTemp(LoggerTemp_C, 250)

#### 'MEASURE THERMISTORS

#### PortSet (1,1) ' Turn on mux

#### i=1

#### SubScan (0,Sec,13)

#### Delay (0,10,mSec)

#### PulsePort(4,10000) ' Clock mux

#### BrHalf(therm(i),4,Autorange,1,Vx1,4,2500,True,0,_60Hz, 1.0, 0)

#### i=i+4

#### NextSubScan

#### PortSet (1,0) ' turn mux  off.

#### For i=1 To 52

#### Therm_kOhm(i) = (25*therm(i))/(1-therm(i))

#### Next i

#### For i=1 To 52

#### D(i) = LN (1000*Therm_kOhm(i)) 'ln resistance (ohm)

#### Next i

#### For i=1 To 44

#### Temp_C(i) = (1/(a + b*D(i) + c*(D(i))^3)) - 273.15     'Steinhart & Hart Equation for new  thermistors

#### Next i

#### For i=45 To 48

#### Temp_C(i) = (1/(agw + bgw*D(i) + cgw*(D(i))^3)) - 273.15 'Equation for reused GW thermistors

#### Next i

#### Temp_C(49) = (1/(a + b*D(49) + c*(D(49))^3)) - 273.15 '2 of the GW thermistors had to be replaced thus these equations

#### Temp_C(50) = (1/(agw + bgw*D(50) + cgw*(D(50))^3)) - 273.15

#### Temp_C(51) = (1/(agw + bgw*D(51) + cgw*(D(51))^3)) - 273.15

#### Temp_C(52) = (1/(a + b*D(52) + c*(D(52))^3)) - 273.15

#### 'OUTPUT

#### CallTable GL_centerlooptempday

#### CallTable GL_eastgroundtempday

#### CallTable GL_eastloopgtempday

#### CallTable GL_westgroundtempday

#### CallTable GL_westloopgtempday

#### CallTable GL_surfacetemphr

#### CallTable GL_quartertemphr

#### CallTable GL_groundtemprawhr

#### CallTable GL_HourlyDiag

#### NextScan

#### EndProg

#### In-building Data Collection

Logger – one CR1000 with multiplexer

Manifold Temperature – Return on each loop and supply and return on the full manifold

Main Questions: How do the ground loop temperatures change over time?

Sensor: NTC Thermistors, US Sensor PS103J2

Measurement Range:  -80°C to 150°C ±0.1°C

Output Units:  temp in ° C

Scan Interval: 5 seconds

Averaging Interval: hourly (when pump is running)

Algorithm:  see algorithm above for Loop 1-6, see algorithm below for Manifold temps

Locations:  in the mechanical room on the manifold

Loop 1

| Wire Color | Cable Color | Name |
| --- | --- | --- |
| brown | green | RTFGSHP_loop1east_C |

Loop 2

| Wire Color | Cable Color | Name |
| --- | --- | --- |
| blue | green | RTFGSHP_loop2_C |

Loop 3

| Wire Color | Cable Color | Name |
| --- | --- | --- |
| orange | green | RTFGSHP_loop3_C |

Loop 4

| Wire Color | Cable Color | Name |
| --- | --- | --- |
| green | green | RTFGSHP_loop4_C |

Loop 5

| Wire Color | Cable Color | Name |
| --- | --- | --- |
| brown | blue | RTFGSHP_loop5_C |

Loop 6

| Wire Color | Cable Color | Name |
| --- | --- | --- |
| blue | blue | RTFGSHP_loop6west_C |

Manifold – use Onicon equipment

| Wire Color | Cable Color | Name |
| --- | --- | --- |
|  |  | RTFGSHP_GLsupplytemp_F (supply to GL) |
|  |  | RTFGSHP_GLreturntemp_F |

#### Boiler BTU meter

Temperature sensors

RTFGSHP_boilerreturntemp_C

RTFGSHP_boilersupplytemp_C

Flow Rate – RTFGSHP_boilerflowrate_lmin

Energy Output – RTFGSHP_boilerenergyrate_kW

Main Question Intended: How much heat energy does the boiler supply?

Sensor: Onicon System 10 BTU meter

Location:  in-line with the heat pump

Measurement Range:  32 °F to 200 °F

Output Units: °C,  l/min, kW

Algorithms: will be based on Onicon calibration (constants “C” are defined by Onicon)

Temp=C(x)-C

Flow=C(x)-C

Energy=C(x)-C

Scan Interval: 5 second

Averaging Interval: 15 min, hourly, daily

Summing Interval: 15 min, hourly, daily

#### Ground Loop BTU meter

Temperature sensors:

RTFGSHP_GLsupplytemp_C (supply to GL)

RTFGSHP_GLreturntemp_C

Flow Rate – RTFGSHP_GLflowrate_lmin

Energy Output – RTFGSHP_GLenergyrate_kW

Main Question Intended: How much heat energy does the ground loop supply to the heat pump?

Sensor: Onicon System 10 BTU meter

Location:  in-line with the heat pump

Measurement Range:  32 °F to 200 °F (will need extended temperture for low range)

Output Units: °C, l/min, kW

Algorithms: will be based on Onicon calibration (constants “C” are defined by Onicon)

Temp=C(x)-C

Flow=C(x)-C

Energy=C(x)-C

Scan Interval: 5 second

Averaging Interval: 15 min, hourly, daily

Summing Interval: 15 min, hourly, daily

Hydronic Loop BTU meter

Temperature sensors

After buffer tank – RTFGSHP_tobuildingsupplytemp_C

RTFGSHP_Tobuildingexittemp_C

Flow Rate – RTFGSHP_tobuildingflowrate-lmin

Energy Output – RTFGSHP_tobuildingenergyrate_kW

Main Question Intended: How much heat energy does the heat pump supply to the building?

Sensor : Onicon System 10 BTU meter

Location:  in-line with the heat pump

Measurement Range:  32 °F to 200 °F

Output Units: °C, l/min, kW

Algorithms: will be based on Onicon calibration (constants “C” are defined by Onicon)

Temp=C(x)-C

Flow=C(x)-C

Energy=C(x)-C

Scan Interval: 5 second

Averaging Interval: 15 min, hourly, daily

Summing Interval:15 min, hourly, daily

#### Between Heat Pump and Buffer Tank BTU meter

Energy Output – RTFGSHP_HPtoBuffer_kW

Temp from buffer to HP -RTFGSHP_buffersupplytemp_C

Temp from HP to buffer - RTFGSHP_bufferreturntemp_C

Flow rate between HP and buffer - RTFGSHP_bufferflowrate_lmin

Energy rate between HP and buffer -RTFGSHP_bufferenergyrate_kw

Total volume between HP and buffer - RTFGSHP_buffervolumeflow_liters

Total energy between HP and buffer - RTFGSHP_buffertotalenergy_kwh

Main Question Intended: How much heat energy does the heat pump supply to the building?

Sensor : Badger system 380 Impeller BTU meter

Location:  between heat pump and buffer tank

Measurement Range:  -4 °F to 140 °F

Output Units: kwh, C, l/min, kW

Algorithms: pulse outputs are summed, PulseCount (RTFGSHP_HPtoBuffer_kWh,1,1 ,2,0,1.0,0)

Modbus data is collected via,   ModBusMaster(result,ComME,BAUD_RATE,SLAVE_MODBUS_ADDR,3,Badger(),1,11,3,100,0)

Scan Interval: 5 second

Averaging Interval: 15 min, hourly, daily

Summing Interval:15 min, hourly, daily

#### Ground Circ Pump Electrical Meter

Main Question Intended: How much energy does the pump use?

Sensor: Magnelab SPT-0375-300, Magnelab SCT-0400-005

Location:  on electrical supply

Measurement Range: 5 amp max

Output Units: watts, a,ps

Algorithm: ACPower (Electricalpumps(),2,60,7,8,230/333,208,9,5/333,20)

Scan Interval: 5 seconds

Averaging Interval: 15 min, hourly, daily

Summing Interval:15 min, hourly, daily

#### Hydronic Circ Pump Electrical Meter

RTFGSHP_circpumppower_watts

RTFGSHP_circpumpcurrent_amps

Main Question Intended: How much energy does the pump use?

Sensor  SPT-0375-300, Magnelab SCT-0400-005, SPT-0375-150

Location:  on electrical supply

Measurement Range: 5 amp max

Output Units: watts, amps

Algorithm: ACPower (Electricalpumps(),2,60,7,8,230/333,208,9,5/333,20)

Scan Interval: 5 seconds

Averaging Interval: 15 min, hourly, daily

Summing Interval:15 min, hourly, daily

#### Heat Pump Electrical Meter

RTFGSHP_HPPower_watts

RTFGSHP_HPcurrent_amps

RTFGSHP_pump1power_watts

RTFGSHP_pump2power_watts

RTFGSHP_pump3power_watts

RTFGSHP_pump1current_amps

RTFGSHP_pump2current_amps

RTFGSHP_pump3current_amps

Main Question Intended: How much energy does the pump use?

Sensor  SPT-0375-300, Magnelab SCT-0750-100

Location: on electrical supply

Measurement Range: max 100 amps

Output Units: watts

Algorithm: ACPower (ElectricalHP(),2,60,7,8,230/333,208,9,100/333,80)

Scan Interval: 5 seconds

Averaging Interval: 15 min, hourly, daily

Summing Interval:15 min, hourly, daily

## DRAFT – GSHP CR1000 program

'Program Name RTF_GSHP

'date 1/30/201

'changed tables to RecBefore and After to 0

'installed new pump CTs, changed CT multiplier in program

'date 2.4.14

'changed tables with CS help to hopefully record only when running

'2.6.14

'cleaned up tables, working with modbus on Bader meter

'2.21.14 added table to look at 30 sec data in ground loop, will collect 2 hrs of data than delete table.

'3.3.14 working on Badgermeter BACnet

'3.24.14 added table for GL BTU meter with Jagan's specific heat numbers

'4.14.14 fixed Badger table

'4.15.14 added power table fixed Badger table to sample instead of average

'10.14.14 changed tables to smooth anaylsis

Public StationID

Public LoggerTemp_C, BattVolts_V

Public Onicon(12), volt(12)

Public ElectricalHP(7), Electricalpump1(7), Circpump(7), Electricalpump2(7),Electricalpump3(7)

Public Therm_kOhm(6), Temp_C(6), therm(6)

Public RTFGSHP_HPtoBuffer_kWh,RTFGSHP_boilerenergy_kWh

Public RTFGSHP_GLenergy_kWh,RTFGSHP_tobuildingenergy_kWh

Public RTFGSHP_HPenergy_kWh, RTFGSHP_pumpenergy_kWh, RTFGSHP_circenergy_kWh

Public Badger(11), result

Public RTFGSHP_GLcalcenergy_kWh,RTFGSHP_HPPower_kw

Dim disable,disablemani,disablebldg,disableboiler

Dim i

Dim D(6)

'  For thermistors -- conversion of kOHM to deg C

Const a = 0.00112538852122

Const b = 0.000234711863267

Const c = 0.000000085663516

Const BAUD_RATE = 9600       'baud rate to use for modbus

Const SLAVE_MODBUS_ADDR = 1  'modbus address of the slave device

Alias Temp_C (1)=RTFGSHP_loop5_C

Alias Temp_C (2)=RTFGSHP_loop6west_C

Alias Temp_C (3)=RTFGSHP_loop3_C

Alias Temp_C (4)=RTFGSHP_loop4_C

Alias Temp_C (5)=RTFGSHP_loop1east_C

Alias Temp_C (6)=RTFGSHP_loop2_C

Alias Onicon(1)=RTFGSHP_GLflowrate_lmin

Alias Onicon(2)=RTFGSHP_GLenergyrate_kW

Alias Onicon(3)=RTFGSHP_GLreturntemp_C

Alias Onicon(4)=RTFGSHP_GLsupplytemp_C

Alias Onicon(5)=RTFGSHP_boilerflowrate_lmin

Alias Onicon(6)=RTFGSHP_boilerenergyrate_kW

Alias Onicon(7)=RTFGSHP_boilerreturntemp_C

Alias Onicon(8)=RTFGSHP_boilersupplytemp_C

Alias Onicon(9)=RTFGSHP_tobuildingflowrate_lmin

Alias Onicon(10)=RTFGSHP_tobuildingenergyrate_kW

Alias Onicon(11)=RTFGSHP_tobuildingexittemp_C

Alias Onicon(12)=RTFGSHP_tobuildingsupplytemp_C

Alias ElectricalHP(1)= RTFGSHP_HPPower_watts

Alias ElectricalHP(4)= RTFGSHP_HPcurrent_amps

Alias Electricalpump1(1)=RTFGSHP_pump1power_watts

Alias Electricalpump2(1)=RTFGSHP_pump2power_watts

Alias Electricalpump3(1)=RTFGSHP_pump3power_watts

Alias Electricalpump1(4)=RTFGSHP_pump1current_amps

Alias Electricalpump2(4)=RTFGSHP_pump2current_amps

Alias Electricalpump3(4)=RTFGSHP_pump3current_amps

Alias Circpump(1)=RTFGSHP_circpumppower_watts

Alias Circpump(4)=RTFGSHP_circpumpcurrent_amps

Alias Badger(1) = RTFGSHP_buffersupplytemp_C

Alias Badger(2) = RTFGSHP_bufferreturntemp_C

Alias Badger(3) = RTFGSHP_bufferflowrate_lmin

Alias Badger(4) = RTFGSHP_bufferenergyrate_kw

Alias Badger(5) = RTFGSHP_buffervolumeflow_liters

Alias Badger(6) = RTFGSHP_buffertotalenergy_kwh

'STATION ID

StationName (RTF_GSHP)

'\\\\\\\\\\\\\\\\\\\\\\\\ OUTPUT SECTION ////////////////////////

DataTable(RTFGSHP_HourlyRAW, true, -1)

DataInterval(0,60,Min,10)

Sample(1, StationID, FP2)

Average (1,LoggerTemp_C,FP2,False)

Average (1,BattVolts_V,FP2,False)

Average (12,Onicon(), FP2, False)

Average (6, therm(), FP2, False)

EndTable

DataTable (RTFGSHP_GLmanifoldhr,true, -1)

DataInterval(0,60,Min,10)

Average (1,RTFGSHP_loop1east_C,FP2,disablemani)

Average (1,RTFGSHP_loop2_C,FP2,disablemani)

Average (1,RTFGSHP_loop3_C,FP2,disablemani)

Average (1,RTFGSHP_loop4_C,FP2,disablemani)

Average (1,RTFGSHP_loop5_C,FP2,disablemani)

Average (1,RTFGSHP_loop6west_C,FP2,disablemani)

Average (1,RTFGSHP_GLreturntemp_C,FP2,disablemani)

Average (1,RTFGSHP_GLsupplytemp_C,FP2,disablemani)

EndTable

DataTable (RTFGSHP_Energyday, true, -1)

DataInterval(0,24,Hr,10)

Totalize (1,RTFGSHP_GLenergy_kWh,FP2,disable)

Totalize (1,RTFGSHP_HPenergy_kWh,FP2,disable)

Totalize (1,RTFGSHP_HPtoBuffer_kWh,FP2,disable)

Totalize (1,RTFGSHP_tobuildingenergy_kWh,FP2,disablebldg)

Totalize (1,RTFGSHP_circenergy_kWh,FP2,disable)

Totalize (1,RTFGSHP_pumpenergy_kWh,FP2,disable)

Maximum (1,RTFGSHP_buffertotalenergy_kwh,FP2,False,0)

EndTable

DataTable (RTFGSHP_Energyhour, true, -1)

DataInterval(0,60,min,10)

Totalize (1,RTFGSHP_GLenergy_kWh,FP2,disable)

Totalize (1,RTFGSHP_HPenergy_kWh,FP2,disable)

Totalize (1,RTFGSHP_HPtoBuffer_kWh,FP2,disable)

Totalize (1,RTFGSHP_tobuildingenergy_kWh,FP2,disablebldg)

Totalize (1,RTFGSHP_circenergy_kWh,FP2,disable)

Totalize (1,RTFGSHP_pumpenergy_kWh,FP2,disable)

Maximum (1,RTFGSHP_buffertotalenergy_kwh,FP2,False,0)

EndTable

DataTable (RTFGSHP_Powerhour, true, -1)

DataInterval(0,60,min,10)

Average (1,RTFGSHP_GLenergyrate_kW,FP2,disable)

Average (1,RTFGSHP_HPPower_kw,FP2,disable)

Average (1,RTFGSHP_bufferenergyrate_kw,FP2,disable)

Average (1,RTFGSHP_tobuildingenergyrate_kW,FP2,disablebldg)

Average (1,RTFGSHP_circpumppower_watts, FP2,disablebldg)

Average (1,RTFGSHP_pump1power_watts, FP2,disable)

Average (1,RTFGSHP_pump2power_watts, FP2,disable)

Average (1,RTFGSHP_pump3power_watts, FP2,disable)

EndTable

DataTable (RTFGSHP_GSHPhour, true, -1)

DataInterval(0,60,Min,10)

Average (1,RTFGSHP_GLreturntemp_C,FP2,disable)

Average (1,RTFGSHP_GLsupplytemp_C,FP2,disable)

Average (1,RTFGSHP_GLflowrate_lmin,FP2,disable)

Average (1,RTFGSHP_GLenergyrate_kW,FP2,disable)

Average (1,RTFGSHP_tobuildingexittemp_C,FP2,disablebldg)

Average (1,RTFGSHP_tobuildingsupplytemp_C,FP2,disablebldg)

Average (1,RTFGSHP_tobuildingflowrate_lmin,FP2,disablebldg)

Average (1,RTFGSHP_tobuildingenergyrate_kW,FP2,disablebldg)

Average (1,RTFGSHP_buffersupplytemp_C,FP2,disable)

Average (1,RTFGSHP_bufferreturntemp_C,FP2,disable)

Average (1,RTFGSHP_bufferflowrate_lmin,FP2,disable)

Average (1,RTFGSHP_bufferenergyrate_kw,FP2,disable)

EndTable

DataTable (RTFGSHP_GSHP15m, true, -1)

DataInterval(0,15,Min,10)

Average (1,RTFGSHP_GLreturntemp_C,FP2,disable)

Average (1,RTFGSHP_GLsupplytemp_C,FP2,disable)

Average (1,RTFGSHP_GLflowrate_lmin,FP2,disable)

Average (1,RTFGSHP_GLenergyrate_kW,FP2,disable)

Average (1,RTFGSHP_tobuildingexittemp_C,FP2,disablebldg)

Average (1,RTFGSHP_tobuildingsupplytemp_C,FP2,disablebldg)

Average (1,RTFGSHP_tobuildingflowrate_lmin,FP2,disablebldg)

Average (1,RTFGSHP_tobuildingenergyrate_kW,FP2,disablebldg)

Average (1,RTFGSHP_buffersupplytemp_C,FP2,disable)

Average (1,RTFGSHP_bufferreturntemp_C,FP2,disable)

Average (1,RTFGSHP_bufferflowrate_lmin,FP2,disable)

Average (1,RTFGSHP_bufferenergyrate_kw,FP2,disable)

EndTable

DataTable (RTFGSHP_Boiler, true, -1)

DataInterval(0,15,Min,0)

Average (1,RTFGSHP_boilerenergyrate_kW,FP2,disableboiler)

Average (1,RTFGSHP_boilerflowrate_lmin,FP2,disableboiler)

Average (1,RTFGSHP_boilerreturntemp_C,FP2,disableboiler)

Average (1,RTFGSHP_boilersupplytemp_C,FP2,disableboiler)

Totalize (1,RTFGSHP_boilerenergy_kWh,FP2,disableboiler)

EndTable

DataTable (RTFGSHP_Electrichour, true, -1)

DataInterval(0,60,Min,10)

Maximum (1,RTFGSHP_HPPower_watts,FP2,False,1)

Average (1,RTFGSHP_HPPower_watts,FP2,disable)

Average (1,RTFGSHP_HPcurrent_amps,FP2,disable)

Average (1,RTFGSHP_pump1power_watts,FP2,disable)

Average (1,RTFGSHP_pump1current_amps,FP2,disable)

Average (1,RTFGSHP_pump2power_watts,FP2,disable)

Average (1,RTFGSHP_pump2current_amps,FP2,disable)

Average (1,RTFGSHP_pump3power_watts,FP2,disable)

Average (1,RTFGSHP_pump3current_amps,FP2,disable)

Average (1,RTFGSHP_circpumppower_watts,FP2,disablebldg)

EndTable

DataTable (RTFGSHP_Electric15m, true, -1)

DataInterval(0,15,Min,10)

Maximum (1,RTFGSHP_HPPower_watts,FP2,False,1)

Average (1,RTFGSHP_HPPower_watts,FP2,disable)

Average (1,RTFGSHP_HPcurrent_amps,FP2,disable)

Average (1,RTFGSHP_pump1power_watts,FP2,disable)

Average (1,RTFGSHP_pump1current_amps,FP2,disable)

Average (1,RTFGSHP_pump2power_watts,FP2,disable)

Average (1,RTFGSHP_pump2current_amps,FP2,disable)

Average (1,RTFGSHP_pump3power_watts,FP2,disable)

Average (1,RTFGSHP_pump3current_amps,FP2,disable)

Average (1,RTFGSHP_circpumppower_watts,FP2,disablebldg)

EndTable

DataTable (twominutepower,true,-1)

DataInterval (0,2,min,10)

Average (1,RTFGSHP_HPPower_watts,FP2,False)

Average (1,RTFGSHP_pump1power_watts,FP2,False)

Average (1,RTFGSHP_pump2power_watts,FP2,False)

Average (1,RTFGSHP_pump3power_watts,FP2,False)

Average (1,RTFGSHP_GLflowrate_lmin,FP2,False)

Average (1,RTFGSHP_GLenergyrate_kW,FP2,False)

Average (1,RTFGSHP_tobuildingenergyrate_kW,FP2,False)

Average (1,RTFGSHP_tobuildingflowrate_lmin,FP2,False)

Average (1,RTFGSHP_tobuildingexittemp_C,FP2,False)

Average (1,RTFGSHP_tobuildingsupplytemp_C,FP2,False)

Average (1,RTFGSHP_GLreturntemp_C,FP2,False)

Average (1,RTFGSHP_GLsupplytemp_C,FP2,False)

Average (1,RTFGSHP_GLcalcenergy_kWh,FP2,False)

Average (1,RTFGSHP_buffersupplytemp_C,FP2,disable)

Average (1,RTFGSHP_bufferreturntemp_C,FP2,disable)

Average (1,RTFGSHP_bufferenergyrate_kw,FP2,disable)

Average (1,RTFGSHP_bufferflowrate_lmin,FP2,disable)

EndTable

DataTable (twominuteenergy,true,-1)

DataInterval (0,2,min,10)

Totalize (1,RTFGSHP_HPtoBuffer_kWh,FP2,disable)

Maximum (1,RTFGSHP_buffertotalenergy_kwh,FP2,False,0)

Totalize (1,RTFGSHP_tobuildingenergy_kWh,FP2,disablebldg)

Totalize (1,RTFGSHP_HPenergy_kWh,FP2,disable)

Totalize (1,RTFGSHP_GLenergy_kWh,FP2,disable)

Totalize (1,RTFGSHP_GLcalcenergy_kWh,FP2,disable)

EndTable

'\\\\\\\\\\\\\\\\\\\\\\\\\\\ PROGRAM ////////////////////////////

BeginProg

SerialOpen(ComME,BAUD_RATE,4,0,100)

Scan(5,Sec,1, 0)

Battery(BattVolts_V)

PanelTemp(LoggerTemp_C, 250)

'Measure Electricals

ACPower (ElectricalHP(),1,60,1,230/333,208,2,50/333,100,1)

ACPower (Electricalpump1(),1,60,1,230/333,230,3,5/333,10,1)

ACPower (Electricalpump2(),1,60,1,230/333,230,4,5/333,10,1)

ACPower (Electricalpump3(),1,60,1,230/333,230,5,5/333,10,1)

ACPower (Circpump(),1,60,6,115/333,115,7,5/333,10,1)

'measure Badger meter 380

PulseCount (RTFGSHP_HPtoBuffer_kWh,1,1 ,2,0,1.0,0)

ModBusMaster(result,ComME,BAUD_RATE,SLAVE_MODBUS_ADDR,3,Badger(),1,11,3,100,0)

'measure manifold temperatures

BrHalf(therm(),6,mV2500,11,Vx3,6,2500,True,0,_60Hz, 1.0, 0)

For i=1 To 6

Therm_kOhm(i) = (10*therm(i))/(1-therm(i))

D(i) = LN (1000*Therm_kOhm(i))                          'ln resistance (ohm)

Temp_C(i) = (1/(a + b*D(i) + c*(D(i))^3)) - 273.15     'Steinhart & Hart Equation

Next i

'measure onicons

PortSet (1,1) ' Turn on mux

i = 1

SubScan (0,Sec,12)

'Delay (0,10,mSec)

PulsePort(4,10000) ' Clock mux

VoltDiff (volt(i),1,AutoRange,5,False,0,_60Hz,1,0)

i=i+1

NextSubScan

PortSet (1,0) ' turn mux  off.

Onicon(1)=(0.0473*volt(1)-18.927)

Onicon(2)=(0.055*volt(2)-21.98)

Onicon(3)=(0.0208*volt(3)-20.566)

Onicon(4)=(0.0208*volt(4)-20.556)

Onicon(5)=(0.0355*volt(5)-14.195)

Onicon(6)=(0.0824*volt(6)-32.97)

Onicon(7)=(0.0347*volt(7)-9.4444)

Onicon(8)=(0.0347*volt(8)-9.4444)

Onicon(9)=(0.0355*volt(9)-14.195)

Onicon(10)=(0.055*volt(10)-21.98)

Onicon(11)=(0.0347*volt(11)-9.4444)

Onicon(12)=(0.0347*volt(12)-9.4444)

'Convert energy rate to total energy

RTFGSHP_GLenergy_kWh=RTFGSHP_GLenergyrate_kW*5/3600

RTFGSHP_tobuildingenergy_kWh=RTFGSHP_tobuildingenergyrate_kW*5/3600

RTFGSHP_HPenergy_kWh=RTFGSHP_HPPower_watts*5/3600/1000

RTFGSHP_pumpenergy_kWh=(RTFGSHP_pump1power_watts+RTFGSHP_pump2power_watts+RTFGSHP_pump3power_watts)*5/3600/1000

RTFGSHP_circenergy_kWh=RTFGSHP_circpumppower_watts*5/3600/1000

RTFGSHP_boilerenergy_kWh=RTFGSHP_boilerenergyrate_kW*5/3600

RTFGSHP_GLcalcenergy_kWh=RTFGSHP_GLflowrate_lmin*3.5924*.986/60*(RTFGSHP_GLsupplytemp_C-RTFGSHP_GLreturntemp_C)*5/3600

RTFGSHP_HPPower_kw=RTFGSHP_HPPower_watts/1000

'tell tables to log on HP running

disable = true

If RTFGSHP_GLflowrate_lmin > 10 Then disable = false

disablemani=true

If RTFGSHP_GLflowrate_lmin > 50 Then disablemani = false

disablebldg=true

If RTFGSHP_tobuildingflowrate_lmin > .2 Then disablebldg = false

disableboiler=true

If RTFGSHP_boilerflowrate_lmin>0 Then disableboiler=false

'OUTPUT

CallTable RTFGSHP_Boiler

CallTable RTFGSHP_Energyday

CallTable RTFGSHP_Energyhour

CallTable RTFGSHP_GSHPhour

CallTable RTFGSHP_GSHP15m

CallTable RTFGSHP_Electric15m

CallTable RTFGSHP_Electrichour

CallTable RTFGSHP_GLmanifoldhr

CallTable RTFGSHP_HourlyRaw

CallTable twominuteenergy

CallTable twominutepower

CallTable RTFGSHP_Powerhour

NextScan

EndProg

Draft Wiring Diagrams – Ground Loop Temperatures

Draft Wiring Diagrams – In Building Data System