## DataFileVariables
Data File Metadata | Field | File Name | File Extension | Number of Header Lines Total | Column # | Name / Title | Definition of Name / Title | Units | Storage Type | Location, building | Location, level | Location, details | Notes | Min Valid Value | Max Valid Value | Error Code | Precision (Decimal Places) | Calculation Notes
| Description | What is the exact name of the file(s) you are currently submitting? | What is the file extension type? Please select one of the following : .dat, .csv, or .xlsx | How many header lines are in the data file? | Which column of data are the following descriptions referring to? | What is the data field called? | Give a detailed description of the data field name. | Unit label for measurements. (cm, degC,%, etc.) | string (text variable), integer (whole number), float point (digits representing real number), date (temporal reference) | which building houses the sensor | what level or floor of the building is the sensor located | where excatly is the sensor using a fixed referece point, list the point, attach photos if possible | Note strange occurance or errors | Minimum expected value for this measurement. (Normal Range) | Maximum expected value for this measurement. (Normal Range) | Any error codes that may be present in the data | Please give the number of decimal places expressed in the data. | Information about calculations performed to derive this value.
| Necessity | REQUIRED | REQUIRED | REQUIRED | REQUIRED | REQUIRED | REQUIRED | REQUIRED | REQUIRED | REQUIRED | REQUIRED | REQUIRED | OPTIONAL | OPTIONAL | OPTIONAL | OPTIONAL | OPTIONAL | REQUIRED
|  | LV_min | .dat | 4 | 1 | TIMESTAMP | date and time | date and time | date | MTL | na | na | na | na | na | na | na | na
[5 empty] | 2 | RECORD | number of recordings since beginning of data collection | number | integer | MTL | na | na | na | na | na | na | na | na
[5 empty] | 3 | BROANsupply_C1_Avg | supply to bldg | C | integer | MTL | na | na | na | na | na | nan | 4 | BrHalf(therm(i),2,mV2500,9,Vx2,2,2500,True,0,_60Hz, 1.0, 0),Therm_kOhm(i) = (10*therm(i))/(1-therm(i)),D(i) = LN (1000*Therm_kOhm(i)) 'ln resistance (ohm), Temp_C(i) = (1/(a + b*D(i) + c*(D(i))^3)) - 273.15, Const a=0.00114288192250106, Const b=0.000231314273877631,,Const c=0.00000010934242301857, Const f=(-0.0000000000725110851146496)
[5 empty] | 4 | BROANsupply_C2_Avg | supply to bldg | C | integer | MTL | na | na | na | na | na | nan | 4 | BrHalf(therm(i),2,mV2500,9,Vx2,2,2500,True,0,_60Hz, 1.0, 0),Therm_kOhm(i) = (10*therm(i))/(1-therm(i)),D(i) = LN (1000*Therm_kOhm(i)) 'ln resistance (ohm), Temp_C(i) = (1/(a + b*D(i) + c*(D(i))^3)) - 273.15, Const a=0.00114288192250106, Const b=0.000231314273877631,,Const c=0.00000010934242301857, Const f=(-0.0000000000725110851146496)
[5 empty] | 5 | BROANsupply_C3_Avg | supply to bldg | C | integer | MTL | na | na | na | na | na | nan | 4 | BrHalf(therm(i),2,mV2500,9,Vx2,2,2500,True,0,_60Hz, 1.0, 0),Therm_kOhm(i) = (10*therm(i))/(1-therm(i)),D(i) = LN (1000*Therm_kOhm(i)) 'ln resistance (ohm), Temp_C(i) = (1/(a + b*D(i) + c*(D(i))^3)) - 273.15, Const a=0.00114288192250106, Const b=0.000231314273877631,,Const c=0.00000010934242301857, Const f=(-0.0000000000725110851146496)
[5 empty] | 6 | BROANreturn_C1_Avg | return from bldg | C | integer | MTL | na | na | na | na | na | nan, 999, -130 | 4 | BrHalf(therm(i),2,mV2500,9,Vx2,2,2500,True,0,_60Hz, 1.0, 0),Therm_kOhm(i) = (10*therm(i))/(1-therm(i)),D(i) = LN (1000*Therm_kOhm(i)) 'ln resistance (ohm), Temp_C(i) = (1/(a + b*D(i) + c*(D(i))^3)) - 273.15, Const a=0.00114288192250106, Const b=0.000231314273877631,,Const c=0.00000010934242301857, Const f=(-0.0000000000725110851146496)
[5 empty] | 7 | BROANreturn_C2_Avg | return from bldg | C | integer | MTL | na | na | na | na | na | nan, 999, -130 | 4 | BrHalf(therm(i),2,mV2500,9,Vx2,2,2500,True,0,_60Hz, 1.0, 0),Therm_kOhm(i) = (10*therm(i))/(1-therm(i)),D(i) = LN (1000*Therm_kOhm(i)) 'ln resistance (ohm), Temp_C(i) = (1/(a + b*D(i) + c*(D(i))^3)) - 273.15, Const a=0.00114288192250106, Const b=0.000231314273877631,,Const c=0.00000010934242301857, Const f=(-0.0000000000725110851146496)
[5 empty] | 8 | BROANreturn_C3_Avg | return from bldg | C | integer | MTL | na | na | na | na | na | nan, 999, -130 | 4 | BrHalf(therm(i),2,mV2500,9,Vx2,2,2500,True,0,_60Hz, 1.0, 0),Therm_kOhm(i) = (10*therm(i))/(1-therm(i)),D(i) = LN (1000*Therm_kOhm(i)) 'ln resistance (ohm), Temp_C(i) = (1/(a + b*D(i) + c*(D(i))^3)) - 273.15, Const a=0.00114288192250106, Const b=0.000231314273877631,,Const c=0.00000010934242301857, Const f=(-0.0000000000725110851146496)
[5 empty] | 9 | BROANincoming_C1_Avg | fresh air | C | integer | MTL | na | na | na | na | na | nan, 999, -130 | 4 | BrHalf(therm(i),2,mV2500,9,Vx2,2,2500,True,0,_60Hz, 1.0, 0),Therm_kOhm(i) = (10*therm(i))/(1-therm(i)),D(i) = LN (1000*Therm_kOhm(i)) 'ln resistance (ohm), Temp_C(i) = (1/(a + b*D(i) + c*(D(i))^3)) - 273.15, Const a=0.00114288192250106, Const b=0.000231314273877631,,Const c=0.00000010934242301857, Const f=(-0.0000000000725110851146496)
[5 empty] | 10 | BROANincoming_C2_Avg | fresh air | C | integer | MTL | na | na | na | na | na | nan, 999, -130 | 4 | BrHalf(therm(i),2,mV2500,9,Vx2,2,2500,True,0,_60Hz, 1.0, 0),Therm_kOhm(i) = (10*therm(i))/(1-therm(i)),D(i) = LN (1000*Therm_kOhm(i)) 'ln resistance (ohm), Temp_C(i) = (1/(a + b*D(i) + c*(D(i))^3)) - 273.15, Const a=0.00114288192250106, Const b=0.000231314273877631,,Const c=0.00000010934242301857, Const f=(-0.0000000000725110851146496)
[5 empty] | 11 | BROANincoming_C3_Avg | fresh air | C | integer | MTL | na | na | na | 0 | 100 | nan | 4 | BrHalf(therm(i),2,mV2500,9,Vx2,2,2500,True,0,_60Hz, 1.0, 0),Therm_kOhm(i) = (10*therm(i))/(1-therm(i)),D(i) = LN (1000*Therm_kOhm(i)) 'ln resistance (ohm), Temp_C(i) = (1/(a + b*D(i) + c*(D(i))^3)) - 273.15, Const a=0.00114288192250106, Const b=0.000231314273877631,,Const c=0.00000010934242301857, Const f=(-0.0000000000725110851146496)
[5 empty] | 12 | BROANexhaust_C1_Avg | exhaust air | C | integer | MTL | na | na | na | 0 | 100 | nan | 4 | BrHalf(therm(i),2,mV2500,9,Vx2,2,2500,True,0,_60Hz, 1.0, 0),Therm_kOhm(i) = (10*therm(i))/(1-therm(i)),D(i) = LN (1000*Therm_kOhm(i)) 'ln resistance (ohm), Temp_C(i) = (1/(a + b*D(i) + c*(D(i))^3)) - 273.15, Const a=0.00114288192250106, Const b=0.000231314273877631,,Const c=0.00000010934242301857, Const f=(-0.0000000000725110851146496)
[5 empty] | 13 | BROANexhaust_C2_Avg | exhaust air | C | integer | MTL | na | na | na | 0 | 100 | nan | 4 | BrHalf(therm(i),2,mV2500,9,Vx2,2,2500,True,0,_60Hz, 1.0, 0),Therm_kOhm(i) = (10*therm(i))/(1-therm(i)),D(i) = LN (1000*Therm_kOhm(i)) 'ln resistance (ohm), Temp_C(i) = (1/(a + b*D(i) + c*(D(i))^3)) - 273.15, Const a=0.00114288192250106, Const b=0.000231314273877631,,Const c=0.00000010934242301857, Const f=(-0.0000000000725110851146496)
[5 empty] | 14 | BROANexhaust_C3_Avg | exhaust air | C | integer | MTL | na | na | na | na | na | nan, 999, -130 | 4 | BrHalf(therm(i),2,mV2500,9,Vx2,2,2500,True,0,_60Hz, 1.0, 0),Therm_kOhm(i) = (10*therm(i))/(1-therm(i)),D(i) = LN (1000*Therm_kOhm(i)) 'ln resistance (ohm), Temp_C(i) = (1/(a + b*D(i) + c*(D(i))^3)) - 273.15, Const a=0.00114288192250106, Const b=0.000231314273877631,,Const c=0.00000010934242301857, Const f=(-0.0000000000725110851146496)
[5 empty] | 15 | BROANroom_C1_Avg | room | C | integer | MTL | na | na | na | na | na | nan, 999, -130 | 4 | BrHalf(therm(i),2,mV2500,9,Vx2,2,2500,True,0,_60Hz, 1.0, 0),Therm_kOhm(i) = (10*therm(i))/(1-therm(i)),D(i) = LN (1000*Therm_kOhm(i)) 'ln resistance (ohm), Temp_C(i) = (1/(a + b*D(i) + c*(D(i))^3)) - 273.15, Const a=0.00114288192250106, Const b=0.000231314273877631,,Const c=0.00000010934242301857, Const f=(-0.0000000000725110851146496)
[5 empty] | 16 | BROANexhaust_RH_Avg | exhaust air | percent | integer | MTL | na | na | na | na | na | nan, 999, -131 | 4 | VoltSe (BROANRH_raw(),8,mV5000,1,1,0,250,.001,0), BROANexhaust_RH=(BROANRH_raw(7)-.8)/0.031
[5 empty] | 17 | BROANincoming_RH_Avg | fresh air | percent | integer | MTL | na | na | na | na | na | nan, 999, -132 | 4 | VoltSe (BROANRH_raw(),8,mV5000,1,1,0,250,.001,0), BROANincoming_RH=(BROANRH_raw(6)-.8)/0.031
[5 empty] | 18 | BROANreturn_RH_Avg | return from bldg | percent | integer | MTL | na | na | na | na | na | nan, 999, -133 | 4 | VoltSe (BROANRH_raw(),8,mV5000,1,1,0,250,.001,0), BROANreturn_RH=(BROANRH_raw(5)-.8)/0.031
[5 empty] | 19 | BROANsupply_RH_Avg | supply to bldg | percent | integer | MTL | na | na | na | na | na | nan, 999, -134 | 4 | VoltSe (BROANRH_raw(),8,mV5000,1,1,0,250,.001,0), BROANsupply_RH=(BROANRH_raw(4)-.8)/0.031
[5 empty] | 20 | BROANroom_RH_Avg | room | percent | integer | MTL | na | na | na | na | na | nan, 999, -135 | 4 | VoltSe (BROANRH_raw(),8,mV5000,1,1,0,250,.001,0), BROANroom_RH=(BROANRH_raw(8)-.8)/0.031
[5 empty] | 21 | pressure_PA_Avg | pressure difference across the core | Pa | integer | MTL | na | na | na | na | na | nan, 999, -136 | 4 | VoltSe (pressure_raw,1,mV5000,16,1,0,250,.001,0), pressure_PA=(24.909*pressure_raw)-62.272